# Tender text for presence detectors

# Presence detector thePrema P360-101 FM WH / GR

Passive-infrared presence detector for ceiling installation; automatic presence and brightness-dependent control for lighting and HVAC; square 360° detection area, walking 100 m2 (10 x 10 m), seated 64 m2 (8 x 8 m) at 3.5m installation height;

-Mixed light measurement for fluorescent lamps 
(FL/PL/ESL), suitable for halogen/incandescent lamps and 
LEDs, can be switched to spot or wide measurement;

Operating voltage 230 V AC / 50 Hz; Protection rating IP 20, in fitted state IP 40;

Channel A light: relay, 1 closer 230 V / 10 A, 2300 W; can be switched between fully automatic or semi-automatic operation; configurable brightness threshold value approx. 5 – 3000 Lux, teach-in function; self-learning time delay 10 s – 60 min; reduction of the time delay when present briefly (short-term presence); connection options for push buttons or switches for manual switching with automatic detection push button/switch; pulse function for staircase light-time switch;

Channel H, presence: relay, 1 closer floating 220 V DC / 50 W or 230 V AC / 50 VA, switch-on delay 0 – 10 min and time delay 10 s – 120 min, room monitoring with selective motion detection, configurable sensitivity;

Configurable sensitivity; ready for operation immediately thanks to factory presets; can be configured remotely with remote control; extremely simple configuration of energy-saving behaviour with the new "eco plus" function; test mode to check function and detection area; extension of detection area by master/slave or master/master switch;

Installation depth 40 mm, ceiling installation in flush-mount socket or ceiling installation socket 73A, ceiling installation possible with surface-mount frame;

Manufacturer: thebenHTS

Type: thePrema P360-101 FM..

Order no.: 2070005 (thePrema P360-101 FM WH, white)

2070006 (thePrema P360-101 FM GR, grey)

Unit: ST

### Accessories

Extension of detection area via slave device:

Optional (can only be used with thePrema P360-101 FM.. as master)

Type: thePrema P360 Slave FM..

Order no.: 2070030 (thePrema P360 Slave FM WH, white)

2070031 (thePrema P360 Slave FM GR, grey)

### "SendoPro 868-A" management remote control

Optional

For the installer for start-up or adjustment to usage conditions.

Text-based operator guidance in the display. Transmission of individual settings or complete configuration sets to the detector possible. Suitable for all remote controlled thebenHTS presence detectors.

Order No.: 9070675

### Service remote control "theSenda P"

Optional

Order no.: 9070910

### User remote control "theSenda S"

Optional

Order no.: 9070911

### Surface mount frame 110A WH

Optional

Order no.: 9070912

### Ceiling installation socket 73A

Optional

Drill diameter 73 mm

Order no.: 9070917