# Tender text for presence detectors

# LON presence detectors for ceiling installation PlanoCentro EWH PCLON / EBK PCLON / ESR PCLON

Passive infrared presence detectors (PIR) for hollow ceiling installation; flat design; square 360° detection area, walking 100 m2 (10 x 10 m), sitting 64 m2 (8 x 8 m) at 3.5 m installation height;

Automatic presence and brightness-dependent control for lighting and HVAC;

Switching or constant light control; choice of fully or semi-automatic operation;

Mixed light measurement 3-fold approx. 10 – 2000 Lux;

Topology LON FTT, Operating voltage 24 V AC/DC;

2 independent Constant Light Controller #3050 for control of two light groups, switching or constant light control with stand-by functionality, brightness set point value with configurable network variable;

3 x Occupancy Controller #3071 for control of the constant light controller or use as presence channels, switch-off delay 10 s – 100 min, switch-on delay 0 s – 30 min;

3 x Light Sensor #1010, can be calibrated individually, selectable light measurement;

Occupancy Sensor #1060;

Scene Panel #3250 can be used with the SendoClic user remote control;

Scene Controller #3251;

Parallel switching of several presence detectors without logic modules, plug-in for convenient configuration of parameters and functionality, remotely configurable and reading of the set parameters;

Installation cut-out section 100 x 100 mm, cover white (EWH), black (EBK), silver (ESR) 112 x 112 x 5 mm, can be changed according to design, colour and material; protection rating IP 40 in fitted state

Manufacturer: thebenHTS

Type: PlanoCentro E.. PCLON

Order No.:	206 9 102 (PlanoCentro EWH PCLON, white, similar to RAL 9010)

206 9 103 (PlanoCentro EBK PCLON, black, similar to RAL 9005)

206 9 104 (PlanoCentro ESR PCLON, silver, similar to RAL 9006)

Unit: ST

### Accessories

### SendoPro 868-A management remote control

Optional for the installer for start-up or adjustment to usage conditions.

Text-based operator guidance in the display. Transmission of individual settings or complete configuration sets to the detector possible. Suitable for all remote controlled thebenHTS presence detectors.

Order No.: 9070675

### SendoClic user remote control

Optional

Order No.: 9070690

### Mounting kit PlanoSet RQ

Optional

Installation set for simple and rapid installation in hollow ceilings consisting of round PlanoFix E installation socket with 126 mm diameter, 142 x 142 mm PlanoCover cover and installation parts;

Type: PlanoSet RQ E..

Order no.:	907 0 736 (PlanoSet RQ EWH, white, similar to RAL 9010)

907 0 737 (PlanoSet RQ EBK, black, similar to RAL 9005)

907 0 738 (PlanoSet RQ ESR, silver, similar to RAL 9006)

### Mounting kit PlanoSet RR

Optional

Installation set for simple and rapid installation in hollow ceilings consisting of round PlanoFix E installation socket with 126 mm diameter, 172 mm diameter PlanoCover cover and installation parts;

Type: PlanoSet RR E..

Order no.:	907 0 740 (PlanoSet RR EWH, white, similar to RAL 9010)

907 0 741 (PlanoSet RR EBK, black, similar to RAL 9005)

907 0 742 (PlanoSet RR ESR, silver, similar to RAL 9006)